## Slide 1: A Stochastic Approach to Occupant Pre-Movement in Fires
Presented by: Jamie Vistnes
Manager, Fire Safety Policy Unit
Fire & Rescue NSW

## Slide 2: Acknowledgements
This presentation is based on:
  Paper presented at 8th IAFSS Symposium in Beijing (2005) prepared by Jamie Vistnes, Stephen Grubits and Yaping He
  Masters Thesis by Jamie Vistnes (2004)

## Slide 3: Introduction
Evaluation of the required safe egress time is an important step
Required Safe Egress Time (RSET)
  detection time
  pre-movement time
  movement time
Parameters that affect pre-movement times

## Slide 4: Introduction
Some current pre-movement models reviewed
  SFPE Handbook
  Method by Sime
  CESARE Risk
  CRISP
  FIERAsystem
Findings
  Limited use of probability distributions
  Simplistic treatment of actions using discrete values
  Not accounting for varying abilities within a population

## Slide 5: Introduction
Objective: To develop an occupant pre-movement model that will adequately consider both the building and occupant characteristics in estimating the likely pre-movement times of occupants in a fire situation
Improvements on current models
  More actions
  Greater variability
  Stochastic treatment

## Slide 6: Methodology
Stochastic system
  dynamic system that involves random parameters or parameters that are too complicated to be described by deterministic means
Parameters of human behaviour have a large degree of uncertainty or randomness
  Best handled with stochastic methodology

## Slide 7: Methodology
Response Period - Interpretation of the cue as a cause for action
  time for the interpretation and decision process
Delay Period - Occupants undertaking a number of actions prior to evacuating.
  which actions occur
  how often they occur
  time the occupant takes to undertake each action
Occupants have different priorities and varying levels of ability and commitment
  probabilities of occurrence
  probability density distribution function

## Slide 8: Methodology
A limited set of actions are defined
Probability distribution functions for various actions
A Monte Carlo simulation utilising a Latin hypercube sampling algorithm
  Divides into regions, values randomly selected within each region
Microsoft Excel add-in @RISK

## Slide 9: Response Time
Every occupant undertakes this process
General trend in occupant pre-movement suggests a log-normal distribution
Mean and standard deviation derived from experimental studies of evacuations and current research (refer to references within paper)
Dependant on warning system (in current model - bell or sounder or EWIS)

## Slide 10: Delay Actions
The number, type and duration of delay actions may vary from occupant to occupant
Process:
  Identification of actions
  Probability of occurrence
  Duration
These will vary as occupants would have different priorities in a fire situation as well as varying levels of ability and commitment

## Slide 11: Delay Actions
Notify others
Telephoned others
Collect belongings
Investigate/search for fire
Close/open doors/windows
Rescue
Call Fire Brigade
Fight fire
Inaction
Shut down equipment
Got dressed
Woke up

## Slide 12: Delay Action Probability
Percentage of occupants undertaking certain delay actions based on literature
Discrete probabilities associated with each delay action derived from percentage undertaking action
No limits set on the number of delay actions undertaken by an occupant

## Slide 13: Delay Action Probability

## Slide 14: Delay Action Duration
Occupant pre-movement time dependant on both building and occupant characteristics
Building characteristics define travel distances
Occupant characteristics define travel speed
Delay action time
  ai = time taken for action i, di = travel distance, v = travel speed
  eg Call Fire Brigade = Time to travel to phone + time to talk on phone to fire brigade

## Slide 15: Delay Action Duration (ai)
Estimated times (due to lack of data)

## Slide 16: Pre-Movement Time
Total pre-movement time, tp
tr = response time, ti = delay time for action i

## Slide 17: Outline of the Model
Start
Choose appropriate parameters according to occupants and building
Choose response time from pddf
Is action “n” undertaken
Choose delay time from pddf for action “n”
All actions considered?
Store response time plus sum of delay times
All iterations complete?
Statistical analysis
Output results
End
No
No
No
Response
Delay

## Slide 18: Results
Results compared to actual research data (Proulx and Fahy)
Data available for generic and residential occupancies
To permit comparison of results data analysed to derive cumulative probability distribution function

## Slide 19: Results
Distribution for Pre-Movement Time
Pre-Movement Time (seconds)
0.000
0.000
0.001
0.001
0.002
0.002
0.003
0.003
0.004
0
250
500
750
1000
Mode
Mean
Long tail

## Slide 20: Results

## Slide 21: Results

## Slide 22: Results

## Slide 23: Sensitivities
Number of iterations
Doubling means and standard deviations for time constants
Regression
Correlation

## Slide 24: Conclusions
The Model:
  Building-occupant interaction
  Uncertainties explicitly treated
  Many factors considered
  Covers variation in behaviour
  Good correlation
  Extensible to treat movement time

## Slide 25: Conclusions
Limitations
  Markovian process – no memory
  Interactions between individual occupants or occupant groups not considered
  Data available
Guides further research
  Nature and times of delay actions
  Specific occupancies
  Outputs would also be useful for input into other probabilistic models