## Slide 1: Building Fire Spread Yaping He School of Computing, Engineering and Mathematics Western Sydney University

## Slide 2: Grenfell Tower Fire - Renovations with deadly cladding

## Slide 4: Lessons have not been learnt
Shanghai fire, 2010 (58 fatalities)
Melbourne Lacrosse Building fire, 2014 (no fatality)
Lacrosse Building fire
Shanghai fire

## Slide 5: Energy efficiency and fire safety - Conflict and trade-off
Energy efficiency
  Better insulating materials
  Low embedded greenhouse gas emission materials
Fire safety
  Non-combustible materials (usually with high embedded GHG emissions)
  Fire resistant materials (usually with high embedded GHG emissions)

## Slide 6: Comparison of material properties
Material | Density (kg/m3) | Thermal conductivity (W/mK) | Heat of combustion (MJ/kg) | Source
Normal Concrete | ~ 2400 | 0.15 ~ 1.6 | 0 | Website 1 & 2 (2017)
Lightweight concrete | 160 ~ 1920 | 0.1 ~ 0.3 | 0 | Website 1 & 2 (2017)
Aerated concrete | 300 ~ 1600 | 0.11 ~ 0.135 | 0 | Website 1 & 2 (2017) Pruteanu (2013)
Polymer | 836 ~ 1523 | 0.05 ~ 0.51 | 7 ~ 45 | Website 2 & 3 (2017)
Polymer foam | 96 ~ 577 | 0.03 ~ 0.043 | 7 ~ 45 | Website 2 & 3 (2017)
Timber | 600 ~ 1100 | 0.12 ~ 0.17 | 15 ~ 20 | Tewarson (2008)
Polyethylene LD | 950 | 0.45 | 41 | Tewarson (2008)
Polyethylene foam | 24 ~ 27 | 0.04 | 41 | Tewarson (2008) Martínez-Díez et al. (2001)

## Slide 7: Timber Buildings

## Slide 8: Fire Spread
Internal spread within a building
  Horizontal spread between compartments
  Vertical spread through floors/ceilings, stairs and shafts
Exterior spread
  Along the envelop of a building
  Between levels
Exterior spread between buildings
  Via thermal radiation
  Flame and/or ember
  (O’Connor, 2016)

## Slide 9: Internal spread within a building - Protection measures
Fire suppression systems
  Fire extinguishers;
  Hose-reels;
  Sprinklers.
Compartmentation
  Fire rating compartment boundaries: walls, ceilings and floors;
  Fire rating of openings: doors and windows
  Protection of penetrations: cable and pluming penetrations

## Slide 10: Compartmentation - Fire resistance design
Fire resistance level (FRL) vs fire severity (FS) analysis (timeline analysis)
FRL > FS
FS depends on
  Fire load
  Ventilation condition
  Interior lining of the compartment
  (Spearpoint, 2008)

## Slide 11: Combined sprinkler and compartmentation system
Eurocode approach (EN-1991-1-2)
  Empirical correlation and safety factors
Risk based approach (He and Grubits, 2010)
  Comparative failure probabilities

## Slide 12: Exterior Spread between buildings
Verification Method CV1 and CV2

## Slide 13: Fire exterior spread along building envelope - Evaluation methods (Hesami, 2016)

## Slide 14: Estimate of surface flame spread Vertical flame spread velocity
 | (1)
 | (1)
where Vp = flame spread velocity (m/s)
k – thermal conductivity (W/m K)
 – density of the fuel (kg/m3)
c = specific heat (J/kg K)
Tig = ignition temperature (C)
To = initial temperature (C)
qf" = flame heat flux (W/m2)

## Slide 15: Flame height and preheating distance
 | (2)
 | (2)
 | (3)
 | (3)
where xf = flame height (m)
k’ = coefficient (0.043 ~ 0.067 m1/3kW-2/3)
= heat release rate per unit width of the fire source
(kW/m)

## Slide 16: Burning surface height and heat release rate per unit width
 | (4)
 | (4)
 | (5)
 | (5)
where q"= burning intensity, or heat release rate per unit
burning surface area (kW/m2)

## Slide 17: Algorithm
t > tend
Set initial conditions
Start
Estimate xp using Eq. (4)
Estimate using Eq. (5)
Estimate xf using Eq. (3)
Estimate fc using Eq. (2)
Estimate Vp using Eq. (1)
Add time increment
No
Yes
End

## Slide 18: Grenfell Fire – A case study
To demonstrate the application of the method
The detailed configuration of the composite cladding is not known

## Slide 19: Grenfell Tower
Constructed in 1974
24 storeys
Concrete structure
No sprinklers?
Refurbished in 2016
  Aluminium composite cladding (aluminium with polyethylene core)
  New windows

## Slide 20
Spray paints - polyester

## Slide 21: Assumptions
Polyethylene foam is without any cover
The wind effect is neglected
The cladding is continuous
The heat release rate intensity of polyethylene foam can be approximated by that of polyurethane foam
Mean flame temperature: 800 C
Flame emissivity: 0.6
Initial burning surface height: 0.05 m

## Slide 22: Input parameters
Parameter | Value | Source
k (W/m K) | 0.04 | Martínez-Díez, et al. (2001)
 (kg/m3) | 25 | Martínez-Díez, et al. (2001)
c (kJ/kg K) | 1.9 | Martínez-Díez, et al. (2001)
Tig | 377 | Tewarson (2008)
(kW/m2) | 173 | Babrauskas (2016)
k’(m1/3kW-2/3) | 0.05 | Hesami (2016)
t (s) (integration time step) | 0.05 | 
Parameter | Value | Source
k (W/m K) | 0.04 | Martínez-Díez, et al. (2001)
 (kg/m3) | 25 | Martínez-Díez, et al. (2001)
c (kJ/kg K) | 1.9 | Martínez-Díez, et al. (2001)
Tig | 377 | Tewarson (2008)
 | 173 | Babrauskas (2016)
k’(m1/3kW-2/3) | 0.05 | Hesami (2016)
t (s) (integration time step) | 0.05 | 

## Slide 23: Results – Flame height
Chart: Time (s)

## Slide 24: Results – burning surface height
Chart: Time (s)

## Slide 25: Caution
The model has not been validated against large scale vertical combustible surface
The assumptions may be too crude
The effects of other composite materials were not considered

## Slide 26: Concluding remarks
Performance of energy efficiency and fire safety must be assessed together
  Safety first, energy efficiency second;
New fire-resistant/fire-retardant materials with low density and low thermal conductivity need to be developed;
New fire protection technology and techniques need to be developed;

## Slide 27: The New Industrial Transformation Training Centre - ARC Training Centre in Fire Retardant Materials and Safety Technologies
Aim: to improve the fire safety of lightweight materials and structures and fire protection systems utilised in a broad range of industry sectors.

## Slide 28: Conceptual Framework of the Centre

## Slide 29: Participating institutions - 27 Research, education and industrial organisations
Australian Universities
  UNSW
  RMITU
  WSU
  USQ
  U Adelaide
Intal Universities
  Michigan State University
  U of Manchester
  U of Sci and Tech of China
  Hong Kong Polytechnic U
  City U of Hong Kong
  …
Other
  CSIRO
  FRNSW
  AFAC
  DSTO
  Standard Aust
  CSR
  …

## Slide 30: References
Martínez-Díez, J. A., Rodríguez-Pérez, M. A., De Saja, J. A., 2001. The Thermal Conductivity of a Polyethylene Foam Block Produced by a Compression Molding Process. Journal of Cellular Plastics, 37, 21-42.
O’Connor, D. J. 2016. The Building Envelope: Fire Spread, Construction Features and Loss Examples. In: Hurley, M. J. (ed.) SFPE Handbook of Fire Protection Engineering. 5th ed. New York: Springer.
Pruteanu, M. and Vasilache, M., 2013. Thermal conductivity determination for autoclaved aerated concrete elements used in enclosure masonry walls, Buletinul Institutului Politehnic Din Iaşi, 6, 33-42, http://www.bipcons.ce.tuiasi.ro/Archive/423.pdf (Accessed 18/6/2017).
Tewarson, A., 2008. Generation of Heat and Gaseous, Liquid, and Solid Products in Fires. In: DINENNO, P. J. (ed.) SFPE Handbook of Fire Protection Engineering. 4th ed. Boston: Society of Fire Protection Engineers.
Website 1, 2017, The Physics Factbook: http://hypertextbook.com/facts/1999/KatrinaJones.shtml (accessed 18/6/2017).
Website 2, 2017, The Engineering Toolbox: http://www.engineeringtoolbox.com/thermal-conductivity-d_429.html (accessed 18/6/2017)